## 1. error

Multiple references contain merged, duplicated, or invalid year formatting (e.g.,  “2020-2024,” “2014-2020,” “2019-2025”), making the governing edition unclear.

fix / suggestion
Normalize all references to a single governing edition or defer globally to the UMRL.

Reason
USACE/NAVFAC QA will reject specs where the governing reference edition cannot be clearly identified.

location
Page 2–4 – PART 1 GENERAL, REFERENCES (multiple organizations)

New language with context

Add at the end of REFERENCES:

“Unless otherwise noted, referenced standards shall be the latest edition per the UMRL dated April 2025.”

OR clean individual entries, for example:
“ASTM F3125/F3125M (2020) Standard Specification for High Strength Structural Bolts…”

## 2. error

AWS D1.1/D1.1M reference again lists conflicting errata years:

(2020; Errata 1 2021-2025)

fix / suggestion
Identify a single errata cutoff year or defer to UMRL.

Reason
Errata directly affect acceptance criteria; ambiguity can invalidate inspections and weld acceptance.

location
Page 3 – REFERENCES, AMERICAN WELDING SOCIETY

New language with context

Replace with:
“AWS D1.1/D1.1M (2020, including approved errata through 2021)”
or
“AWS D1.1/D1.1M (latest edition per UMRL).”

## 3. error

AGMA references include duplicated and reaffirmed year strings (e.g., “2012; R 2025”).

fix / suggestion
Reduce each AGMA reference to one base publication year plus reaffirmation, or defer to UMRL.

Reason
Gear design tolerances and geometry standards are sensitive to edition changes.

location
Page 2 – REFERENCES, AMERICAN GEAR MANUFACTURERS ASSOCIATION

New language with context

Example correction:
“AGMA ISO 22849-A12 (2012, reaffirmed 2025) Design Recommendations for Bevel Gears.”

## 4. error

“G” submittals do not include RMS approval authority codes.

fix / suggestion
Insert the appropriate RMS authority (AE, DO, RO, etc.) for all “G” submittals.

Reason
Army RMS will reject submittals missing the approving authority.

location
Page 4–5 – PART 1 GENERAL, SUBMITTALS

New language with context

Revise as follows (example):

“Detail Drawings; G, AE”
“Welding Procedures; G, AE”
“Welding Repair Plan; G, AE”
“Application Qualification for Steel Studs; G, AE”

## 5. error

Welding code applicability remains bracketed between AWS D1.1 and AWS D1.2.

fix / suggestion
Explicitly assign welding codes by material.

Reason
Bracketed welding code applicability creates inspection disputes between steel and aluminum work.

location
Page 6 – QUALITY ASSURANCE, Welding Qualifications

New language with context

Replace with:

“Conform welding of structural steel to AWS D1.1/D1.1M and welding of aluminum to AWS D1.2/D1.2M and AA ADM, as applicable.”

## 6. error

Bearings paragraph leaves maximum allowable bearing pressure bracketed:

must not exceed [ ] kPa psi

fix / suggestion
Insert a specific allowable pressure or remove the limitation.

Reason
Bracketed bearing limits are unenforceable and will trigger RFIs during fabrication.

location
Page 7–8 – PART 2 PRODUCTS, Bearings

New language with context

Replace with (example):

“Pressures on lined bearings must not exceed 1400 kPa (200 psi) of projected area unless otherwise indicated.”

## 7. error

Cadmium coating inspection type remains undefined:

ASTM E165/E165M, Type [ ]

fix / suggestion
Specify the applicable inspection type or remove cadmium coating entirely if not required.

Reason
Undefined inspection type prevents enforcement of coating quality.

location
Page 8 – Metallic Coatings, Cadmium Coatings

New language with context

Replace with:

“Inspections conforming to ASTM E165/E165M, Type II.”

## 8. error

Shop assembly paragraph contains mutually exclusive bracketed options.

fix / suggestion
Select one option for shop assembly requirements.

Reason
Leaving both options creates contractual ambiguity on whether shop assembly is required.

location
Page 9 – PART 2 PRODUCTS, Shop Assembly

New language with context

Replace with one of the following:

“Assemble each machinery and structural unit furnished in the shop to verify fabrication and fit prior to shipment.”
or
“Assemble only those machinery and structural units listed below in the shop…”

## 9. error

Ultrasonic testing percentages and acceptance tables remain bracketed:

[50%][ ] … Table [6.2] [or 6.3]

fix / suggestion
Define testing percentages and clearly assign AWS Table 6.2 or 6.3.

Reason
Bracketed NDT requirements are a guaranteed QA and field inspection failure.

location
Page 9–10 – TESTS, INSPECTIONS, AND VERIFICATIONS, Ultrasonic Testing

New language with context

Replace with:

“Test 50 percent of CJP welds using ultrasonic testing in accordance with AWS D1.1/D1.1M Table 6.2 for statically loaded connections.
Welds subject to cyclic loading shall meet Table 6.3 and shall be identified on the construction documents.”

## 10. error

Radiographic inspection severity levels for castings are entirely blank.

fix / suggestion
Insert applicable severity levels or delete the table if radiography is not required.

Reason
Blank severity criteria make acceptance subjective and unenforceable.

location
Page 10 – Inspection of Structural Steel Castings

New language with context

Insert applicable values, for example:

“Severity Level: ASTM E446, Level 2 for all designated castings.”