## 05 21 00 NOTES Review
Note Topic / Excerpt | UFGS Disposition | Recommended Action | UFGS Rationale (Governing-Body Basis)
Additional information – SJI Technical Digests (ponding, vibration, uplift, fire, LFRS, etc.) | Remove | Delete note | Vague, non-specific advisory reference with no document identifiers or edition control; redundant with cited codes and standards.
Use SJI MANUAL reference for projects involving existing joist systems | Remove | Delete note or convert to non-reference informational sentence | SJI MANUAL is historical and non-normative; legacy joist evaluation should rely on sealed analysis and applicable codes.
OSHA joist erection reference when joist lengths exceed 144 ft | Rewrite | Clarify applicability based on OSHA Subpart R triggers | Editorial logic is valid but trigger condition is overly narrow.
Show joist and joist girder information on drawings (loads, reactions, uplift, bridging, anchorage, etc.) | Keep | No change | High-value coordination note that prevents recurring design omissions.
Standard joist tables not applicable when joist depth reduced near ends for two-way slopes > 1/8 in/ft | Keep | Optional minor editorial tightening | Prevents common misapplication of standard joist tables; includes quantified threshold and designer action.
Provide load diagrams and specify deflection criteria | Keep | Consider splitting into two notes for clarity | Addresses frequent joist design submittal omissions.
Include paragraph when joists are bolted to joist girders | Keep | No change | Clear applicability guidance preventing omission of connection requirements.
Recycled content coordination note | Keep | No change | Editorial sustainability coordination consistent with UFGS policy.
Shop painting coordination with Section 09 90 00 | Keep | No change | Cross-section coordination preventing coating scope conflicts.
Bearing plates applicable to masonry or cast-in-place concrete only | Keep | No change | Clarifies scope and prevents misapplication.
Field painting omission note | Keep | No change | Standard UFGS bracket logic.
Penetrations and field modification awareness (not currently explicit) | Add (Optional) | Add short design coordination note | Joist cutting and penetrations are a frequent source of RFIs and field corrections.
Panel point load enforcement (concentrated loads at panel points) | Add (Optional) | Add short design limitation note | Misplaced concentrated loads are a common joist design error.