## KEY
LEGEND
Spec Included
No Spec
All Projects

## S_ConcMix
** THIS TABLE IS TO BE USED ONLY IF SPECIFICATIONS ARE INCLUDED IN THE PROJECT**
CONCRETE MIX DESIGN TABLE
| ELEMENT |  | STRENGTH (PSI), WEIGHT | EXPOSURE CLASS (NOTES 1 & 2)
| FOOTINGS |  | f'c = 4000, NW | F0, S0, W0, C1 | **ENGINEER'S NOTES:**
| FOUNDATION (STEM) WALLS |  | f'c = 4000, NW | F0, S0, W0, C1 | 1. | VERIFY EXPOSURE CLASS W/ GEOTECH AND UFC
| RETAINING WALLS |  | f'c = 4500, NW | F0, S0, W0, C1 | 2. | THIS TABLE SHOULD BE PROVIDED ON ALL PROJECTS AND COORDINATED W/ SPECS
| INTERIOR SLABS ON GRADE |  | f'c = 3000, NW | F0, S0, W0, C1
| EXTERIOR SLABS |  | f'c = 4500, NW | F0, S0, W0, C0
| EXTERIOR CIP WALLS (ABOVE GRADE) |  | f'c = 4500, NW
| INTERIOR CIP WALLS (ABOVE GRADE) |  | f'c = 4500, NW
| PRECAST CONCRETE WALL PANELS |  | f'c = 5000, NW
| TILT UP CONCRETE WALL PANELS |  | f'c = 4000, NW
| LEVELING GROUT |  | f'c = 5000, NW
| DEFORMED CONCRETE REINFORCEMENT |  | Fy = 60,000 | N/A
| WELDABLE CONCRETE REINFORCEMENT |  | Fy = 60,000 | N/A
| EPOXY COATED CONCRETE REINFORCEMENT |  | Fy = 60,000 | N/A
| WELDED WIRE REINFORCEMENT |  | Fy = 65,000 | N/A
| EPOXY COATED WELDED WIRE REINFORCEMENT |  | Fy = 65,000 | N/A
NOTES:
| 1 | EXPOSURE CLASS INDICATES THE SEVERITY OF THE ANTICIPATED
EXPOSURE OF CONCRETE MEMBERS, IN ACCORDANCE WITH ACI 318,
CHAPTER 18.
| 2 | CONCRETE STRENGTH, f'c, IS THE COMPRESSIVE STRENGTH AT
28 DAYS UNLESS NOTED OTHERWISE.
| 3 | NORMAL WEIGHT (NW) CONCRETE SHALL HAVE A DRY DENSITY OF
145 ±4 PCF, UNO. LIGHTWEIGHT CONCRETE (LW) MUST HAVE A
DRY DENSITY OF 115 ±5 PCF UNO.
| 4 | MIX DESIGNS MUST BE IN ACCORDANCE WITH ACI 301.
| 5 | WHERE CONCRETE IS EXPOSURE CLASS F3, RESTRICTIONS ON
MAXIMUM FLY ASH AND/OR OTHER CEMENTITIOUS MATERIALS APPLY.
REFER TO ACI 318, TABLE 26.4.2.2(B) FOR REQUIREMENTS.

## NS_ConcMix
** THIS TABLE IS TO BE USED ONLY IF SPECIFICATIONS ARE NOT INCLUDED IN THE PROJECT**
CONCRETE MIX DESIGN TABLE
| ELEMENT |  |  | f'c (PSI), WEIGHT | CEMENT TYPE | MAX W/C | MAX AGG | AIR CONTENT | SLUMP | EXPOSURE CLASS (NOTES 1 & 2)
| FOOTINGS |  |  | 4000, NW | I/II | 0.55 | 1" | 5% ± 1.5% | ≤6” ±1.5” | F0, S0, W0, C1 | **ENGINEER'S NOTES:**
| FOUNDATION (STEM) WALLS |  |  | 4000, NW | I/II | 0.45 | 1" | 6% ± 1.0% | ≤4” ±1” | F0, S0, W0, C1 | 1 | MINIMUM AIR CONTENT EQUALS 5% IF CONCRETE IS EXPOSED TO FREEZING TEMPERATURE AND MOISTURE REGARDLESS OF VALUE INDICATED IN TABLE. TOLERANCE ON AIR CONTENT AS DELIVERED IS ±1.5%
| RETAINING WALLS |  |  | 4500, NW | II/V | 0.45 | 1" | 6% ± 1.0%
| INTERIOR SLABS ON GRADE |  |  | 3000, NW | II/V | 0.55 | 3/4" |  | ≤6” ±1.5” | F0, S0, W0, C1 | 2 | VERIFY EXPOSURE CLASS W/ GEOTECH AND UFC
| EXTERIOR SLABS |  |  | 4500, NW | II/V | 0.4 | 3/4" |  | ≤6” ±1.5” | F0, S0, W0, C0 | 3 | REVEIWE ROOFING MFR REQUIRMENTS FOR USING LW CONCRETE ON ROOF DECK
| EXTERIOR CIP WALLS (ABOVE GRADE) |  |  | 4500, NW | I/II/III | 0.45 | 3/4"
| INTERIOR CIP WALLS (ABOVE GRADE) |  |  | 4500, NW | I/II/III | 0.45 | 3/4"
PRECAST CONCRETE WALL PANELS
TILT UP CONCRETE WALL PANELS
| LEVELING GROUT |  |  | 5000, NW
NOTES:
| 1 | EXPOSURE CLASS INDICATES THE SEVERITY OF THE ANTICIPATED EXPOSURE OF CONCRETE MEMBERS, IN ACCORDANCE WITH ACI 318, CHAPTER 18.
| 2 | CONCRETE MIX SUPPLIER IS TO ENSURE THAT THE MAXIMUM WATER-SOLUBLE CHLORIDE ION (CL-) CONTENT IN CONCRETE,
BY % WEIGHT OF CEMENT, IS BELOW THE FOLLOWING THRESHOLDS (PER ACI 318 TABLE 19.3.2.1):
|  | A. | REINFORCED CONCRETE: C0 = 1.0; C1 = 0.3; C2 = 0.15
|  | B. | PRESTRESSED CONCRETE: C0 = C1 = C2 = 0.06
| 3 | CONCRETE STRENGTH, f'c, IS THE COMPRESSIVE STRENGTH AT 28 DAYS UNLESS NOTED OTHERWISE.
| 4 | NORMAL WEIGHT CONCRETE SHALL HAVE A DRY DENSITY OF 145 ±4 PCF UNLESS NOTED OTHERWISE. LIGHTWEIGHT CONCRETE (LW) MUST
HAVE A DRY DENSITY OF 115 ±5 PCF UNLESS NOTED OTHERWISE.
| 5 | MIX DESIGNS MUST BE IN ACCORDANCE WITH ACI 301.
| 6 | WHERE CONCRETE IS EXPOSURE CLASS F3, RESTRICTIONS ON MAXIMUM FLY ASH AND/OR OTHER CEMENTITIOUS MATERIALS APPLY.
REFER TO ACI 318, TABLE 26.4.2.2(B) FOR REQUIREMENTS.
| 7 | IF ADDITIONAL SLUMP (UP TO 8") IS DESIRED FOR PUMPING, A SUPER-PLASTICIZER ADMIXTURE MAY BE ADDED.

## NS_ConcMatDes
** THIS TABLE IS TO BE USED ONLY IF SPECIFICATIONS ARE NOT INCLUDED IN THE PROJECT**
CONCRETE MATERIALS DESIGNATION TABLE
| MATERIAL |  | STANDARD
| PORTLAND CEMENT |  | ASTM C150
| LEVELING GROUT (NON-SHRINK, NON-METALLIC) |  | ASTM C1107
| FLY ASH |  | ASTM C618
| AGGREGATE |  | ASTM C33
| WATER |  | ASTM C1602
| WATER REDUCING ADMIXTURE |  | ASTM C494 TYPE A OR TYPE D
| HIGH RANGE WATER REDUCING ADMIXTURE |  | ASTM C494, TYPE F OR TYPE G
| ACCELERATOR ADMIXTURE |  | ASTM C494, TYPE C OR TYPE E
| AIR ENTRAINING ADMIXTURE |  | ASTM C260
| LIGHTWEIGHT AGGREGATES |  | ASTM C330
| CURING COMPOUND |  | ASTM C309, TYPE 1, CLASS A
| DEFORMED REBAR |  | ASTM A615, GRADE 60
| WELDED REBAR |  | ASTM A706, GRADE 60
| EPOXY COATED DEFORMED REBAR |  | ASTM A 775, GRADE 60
| EPOXY COATED WELDED WIRE REINFORCEMENT |  | ASTM A 884
| WELDED WIRE REINFORCEMENT |  | ASTM A185 OR A497
| VAPOR RETARDER BELOW SLAB-ON-GRADE |  | ASTM E1745, CLASS A
NOTES:
| 1 | TYPE III PORTLAND CEMENT MAY BE USED WHEN NOT REQUIRED
BY THESE DOCUMENTS, AT NO ADDITIONAL COST TO THE OWNER,
AT CONTRACTOR’S CHOOSING, WHEN APPROVED BY THE PROJECT
MANAGER AND STRUCTURAL ENGINEER.

## NS_ConcCover
** THIS TABLE IS TO BE USED ONLY IF SPECIFICATIONS ARE NOT INCLUDED IN THE PROJECT**
REMOVE COVER FROM SPECIFICATION IF THEY ARE INCLUDED IN THE PROJECT AND PROVIDE ON DRAWINGS
CONCRETE COVER TABLE
CONCRETE EXPOSURE |  | MEMBER | REINFORCEMENT | COVER (IN)
CAST AGAINST AND PERMANETLY |  | ALL | ALL | 3
IN CONTACT WITH GROUND
EXPOSED TO WEATHER OR |  | ALL | #6 THROUGH #18 | 2
IN CONTACT WITH GROUND |  |  | #5 BAR, W31 OR | 1.5
D31 & SMALLER
CONCRETE NOT EXPOSED TO |  | SLABS & | #11 AND SMALLER | 3/4
WEATHER OR IN CONTACT |  | WALLS | #14 & #18 | 1.5
WITH GROUND |  | BEAMS, | PRIMARY REINF, | 1.5
|  | COLUMNS, | STIRRUPS,
|  | PIERS, & | TIES, SPIRALS &
|  | TENSION TIES | HOOPS
NOTES:
1 | CLEAR COVER FOR NON-PRESTRESSED REINFORCEMENT IN CAST-IN-PLACE
CONCRETE ONLY.
2 | CLEAR COVER REQUIREMENTS FOR MEMBERS OTHER THAN
NON-PRESTRESSED CAST-IN-PLACE CONCRETE MUST BE PER ACI 318.
3 | PROVIDE STANDARD BAR CHAIRS AND SPACERS AS REQUIRED TO MAINTAIN
CONCRETE PROECTION AS SPECIFIED ABOVE.
4 | DIMENSIONS FOR BAR PLACEMENT GIVEN IN SECTIONS AND DETAILS ARE TO
SUPERSEDE THE MINIMUM COVER REQUIREMENTS SPECIFIED ABOVE.
REPORT ANY DISCREPANCY TO THE ENGINEER PRIOR TO POURING
CONCRETE.
5 | NO SURFACES FOR RETAINING WALLS ARE TO BE EARTH FORMED.

## NS_CMU_Materials
** THIS TABLE IS TO BE USED ONLY IF SPECIFICATIONS ARE NOT INCLUDED IN THE PROJECT**
MASONRY MATERIALS DESIGNATION TABLE
| MATERIAL | STANDARD
| HOLLOW CONCRETE MASONRY UNITS | ASTM C90
| GROUT | ASTM C476
| MORTAR | ASTM C270
| DEFORMED REINFORCING BARS (TYPICAL) | ASTM A615, GRADE 60
| WELDED REINFORCING BARS | ASTM A706, GRADE 60
| WIRE REINFORCING BARS | ASTM A951

## ALL_STL_Materials
STEEL MATERIALS DESIGNATION TABLE
MATERIAL |  | STANDARD | STRENGTH
WIDE FLANGE (W) SHAPES |  | ASTM A992 | Fy = 50 KSI
CHANNELS (C & MC) SHAPES
RECTANGULAR, SQUARE & ROUND |  | ASTM A500 | GRADE C, Fy = 50 KSI
HOLLOW STRUCTURAL SHAPES (HSS)
STEEL PIPE |  | ASTM A53 | GRADE B,
Fy = 35 KSI
ANGLES (L) AND ALL OTHER SHAPES |  | ASTM A572 | Fy = 50 KSI
PLATES |  | ASTM A36 | Fy = 36 KSI, UNO
DEFORMED BAR ANCHORS (DBA) |  | ASTM A496 | Fy = 60 KSI
HEADED STUD ANCHORS (HSA) |  | ASTM A108 | Fu = 65 KSI
ANCHOR RODS |  | ASTM F1554 | Fy = 36 KSI
HEAVY HEX NUTS |  | ASTM A563 | MATCH BOLT
STRENGTH
HARDENED WASHERS |  | ASTM F436 | MATCH BOLT
STRENGTH
NOTES:
1 | HEADED STUD ANCHORS DIMENSIONS MUST COMPLY
WITH AISC SPECIFICATIONS
2 | ALL ANCHOR RODS TO BE DESIGNATED AS WELDABLE, UNO.

## ALL_CMU_SPLICES
HIDE
MASONRY REINFORCING SPLICE TABLE
| BAR SIZE |  |  |  | REINFORCING |  | SINGLE REINFORCING | [5 empty] | DOUBLE REINFORCING
[7 empty] | 8" CMU |  | 10" CMU |  | 12" CMU |  | 8" CMU |  | 10" CMU |  | 12" CMU
HIDE |  |  |  | Actual Wall Thickness / 2 | 3.8125 |  |  | 4.8125 |  | 5.8125
|  |  | db | γ | K | 72*DB |  | K |  | K |  | K |  | K |  | K
| 3 |  | 0.375 | 1 | 3.375 | 27 | 12 | 3.375 | 12 | 3.375 | 12 | 2 | 13 | 2 | 13 | 2 | 13
| 4 |  | 0.5 | 1 | 3.5625 | 36 | 13 | 4.5 | 12 | 4.5 | 12 | 2 | 22 | 2 | 22 | 2 | 22 | F'm = | 2000
| 5 |  | 0.625 | 1 | 3.5 | 45 | 19 | 4.5 | 16 | 5.5 | 13 | 2 | 35 | 2 | 35 | 2 | 35 | Fy = | 60000
| 6 |  | 0.75 | 1.3 | 3.4375 | 54 | 37 | 4.4375 | 29 | 5.4375 | 24 | 2 | 54 | 2 | 54 | 2 | 54 | COVER | 2
| 7 |  | 0.875 | 1.3 | 3.375 | 63 | - | 4.375 | 40 | 5.375 | 33 | 2 | - | 2 | 63 | 2 | 63 | NOTE: | INPUT VALUES IN GRAY CELLS ABOVE. SCHEDULE WILL AUTOMATICALLY UPDATE.
| 8 |  | 1 | 1.5 | 3.3125 | 72 | - | 4.3125 | - | 5.3125 | 50 | 2 | - | 2 | - | 2 | 72
NOTES:
| 1 | LAP SPLICE LENGTHS ARE IN INCHES.
| 2 | LAP SPLICES IN REINFORCED MASONRY MUST HAVE MINIMUM
LENGTHS AS DEFINED ABOVE UNLESS NOTE OTHERWISE
| 3 | TABULATED VALUES ARE CALCULATED IN ACCORDANCE WITH
TMS 402/602-16 CHAPTER 6.
| 4 | SPLICE AND DEVELOPMENT LENGTHS ARE THE SAME VALUE FOR
HORIZONTAL AND VERTICAL BARS
| 5 | SINGLE REINFORCING IS A SINGLE BAR CENTERED IN CMU BLOCK CELL,
DOUBLE REINFORCING IS TWO BARS IN A CMU BLOCK CELL
WITH 2 INCH MINIMUM CLEAR COVER FROM OUTSIDE FACE OF BLOCK.
| 6 | TABULATED VALUES BASED ON UNCOATED REINFORCEMENT
WITH A YIELD STRENGTH, Fy =60 ksi.
| 7 | TABULATED VALUES BASED ON MASONRY COMPRESSIVE
STRENGTH, f'm =2,000 psi.
TMS 402/602-16

## ConcRebarSplice_ACI318-14
ENGINEER NOTES:
1. Update values in yellow to match project requirements.
2. Include Typical Detail w/ ld, lst, ldh diagrams
CONCRETE REINFORCING DEVELOPMENT AND LAP SPLICE TABLE
General
[12 empty] | Fy = | 60000 | psi | bar | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11
[12 empty] | Bar Type: | Uncoated or Zinc Coated |  | db | 0.375 | 0.5 | 0.625 | 0.75 | 0.875 | 1 | 1.128 | 1.27 | 1.41
[12 empty] | ψe = | 1
[12 empty] | ψc = | 1
[12 empty] | ψr = | 1
f'c = 4000 psi (NORMAL WEIGHT) | [11 empty] | Mix 1
BAR SIZE |  |  | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | f'c = | 4000 | psi
ld (TOP BARS) |  |  | 19 | 25 | 31 | 37 | 44 | 50 | 56 | 63 | 70 | Weight: | NORMAL WEIGHT
ld (OTHER BARS) |  |  | 15 | 19 | 24 | 29 | 42 | 48 | 54 | 61 | 67 | λ = | 1
lst (TOP BARS) |  |  | 25 | 33 | 41 | 49 | 71 | 81 | 91 | 102 | 114
lst (OTHER BARS) |  |  | 19 | 25 | 31 | 37 | 54 | 62 | 70 | 79 | 87
ldh |  |  | 8 | 10 | 12 | 15 | 17 | 19 | 22 | 25 | 27
f'c = 4500 psi (NORMAL WEIGHT) | [11 empty] | Mix 2
BAR SIZE |  |  | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | f'c = | 4500 | psi
ld (TOP BARS) |  |  | 18 | 24 | 30 | 35 | 41 | 47 | 53 | 60 | 66 | Weight: | NORMAL WEIGHT
ld (OTHER BARS) |  |  | 14 | 18 | 23 | 27 | 40 | 45 | 51 | 57 | 64 | λ = | 1
lst (TOP BARS) |  |  | 23 | 31 | 38 | 46 | 67 | 76 | 86 | 96 | 107
lst (OTHER BARS) |  |  | 18 | 24 | 30 | 35 | 51 | 59 | 66 | 74 | 82
ldh |  |  | 7 | 9 | 12 | 14 | 16 | 18 | 21 | 23 | 26
NOTES:
1 | LENGTHS SHOWN ARE IN INCHES.
2 | LENGTHS SHOWN ABOVE ARE FOR SINGLE REINFORCING BARS WITH MAXIMUM YIELD STRENGTH OF 60 KSI.
3 | LENGTHS SHOWN ASSUME CLEAR SPACING OF BARS ARE AT LEAST 2 TIMES BAR DIAMETER AND CLEAR COVER OF AT LEAST ONE BAR DIAMETER.
4 | FOR EPOXY COATED BARS, MULTIPLY VALUES BY 1.5.
5 | WHEN SPLICING BARS OF DIFFERENT SIZES, USE SPLICE LENGTH FOR LARGER BAR.
6 | SPLICES (LAPS) OF REINFORCING BARS MUST BE CLASS 'B' TENSION LAPS AS INDICATED ABOVE, UNLESS NOTED OTHERWISE.
7 | TOP BARS ARE HORIZONTAL REINFORCING BARS WITH 12 INCHES OR MORE OF FRESH CONCRETE IS PLACED BELOW.
8 | OTHER BARS ARE ANY REINFORCING BARS THAT DO NOT MEET QUALIFICATION FOR TOP BARS.

## ConcRebarSplice_ACI318-19
ENGINEER NOTES:
1. Update values in yellow to match project requirements.
2. Include Typical Detail w/ ld, lst, ldh diagrams
CONCRETE REINFORCING DEVELOPMENT AND LAP SPLICE TABLE
[12 empty] | General | [6 empty] | bar | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11
[12 empty] | Grade: | 60 | Fy = | 60000 | ψg = | 1 |  | db | 0.375 | 0.5 | 0.625 | 0.75 | 0.875 | 1 | 1.128 | 1.27 | 1.41
[12 empty] | Bar Type: | Uncoated or Zinc Coated |  |  | ψe = | 1
[13 empty] | Confining Reinforcement: |  |  | ψr = | 1.6 | UPDATE NOTE 7
[13 empty] | Location: |  |  | ψo = | 1.25 | UPDATE NOTE 7
f'c = 4000 psi (NORMAL WEIGHT) | [11 empty] | Mix 1
BAR SIZE |  |  | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | f'c = | 4000 | psi
ld (TOP BARS) |  |  | 19 | 25 | 31 | 37 | 54 | 62 | 70 | 79 | 87 | Weight: | NORMAL WEIGHT
ld (OTHER BARS) |  |  | 15 | 19 | 24 | 29 | 42 | 48 | 54 | 61 | 67 | λ = | 1
lst (TOP BARS) |  |  | 25 | 33 | 41 | 49 | 71 | 81 | 91 | 102 | 114 | Concrete Strength: |  | ψc = | 0.86667
lst (OTHER BARS) |  |  | 19 | 25 | 31 | 37 | 54 | 62 | 70 | 79 | 87
ldh |  |  | 12 | 15 | 19 | 23 | 27 | 30 | 34 | 38 | 43
f'c = 4000 psi (NORMAL WEIGHT) | [11 empty] | Mix 2
BAR SIZE |  |  | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | f'c = | 4000 | psi
ld (TOP BARS) |  |  | 19 | 25 | 31 | 37 | 54 | 62 | 70 | 79 | 87 | Weight: | NORMAL WEIGHT
ld (OTHER BARS) |  |  | 15 | 19 | 24 | 29 | 42 | 48 | 54 | 61 | 67 | λ = | 1
lst (TOP BARS) |  |  | 25 | 33 | 41 | 49 | 71 | 81 | 91 | 102 | 114 | Concrete Strength: |  | ψc = | 0.86667
lst (OTHER BARS) |  |  | 19 | 25 | 31 | 37 | 54 | 62 | 70 | 79 | 87
ldh |  |  | 12 | 15 | 19 | 23 | 27 | 30 | 34 | 38 | 43
NOTES:
1 | LENGTHS SHOWN ARE IN INCHES.
2 | LENGTHS SHOWN ABOVE ARE FOR SINGLE REINFORCING BARS WITH MAXIMUM YIELD STRENGTH OF 60 KSI.
3 | LENGTHS SHOWN ASSUME CLEAR SPACING OF BARS ARE AT LEAST 2 TIMES BAR DIAMETER AND CLEAR COVER OF AT LEAST ONE BAR DIAMETER.
4 | FOR EPOXY COATED BARS, MULTIPLY VALUES BY 1.5.
5 | WHEN SPLICING BARS OF DIFFERENT SIZES, USE SPLICE LENGTH FOR LARGER BAR.
6 | SPLICES (LAPS) OF REINFORCING BARS MUST BE CLASS 'B' TENSION LAPS AS INDICATED ABOVE, UNLESS NOTED OTHERWISE.
7 | ldh LENGTHS SHOWN ASSUME CONFINING REINFORCEMENT FACTOR EQUAL TO 1.6 AND LOCATION FACTOR EQUAL TO 1.25. CONTRACTOR MAY REDUCE
VALUES PER THE CRITERIA IN ACI TABLE 25.4.3.2.
8 | TOP BARS ARE HORIZONTAL REINFORCING BARS WITH 12 INCHES OR MORE OF FRESH CONCRETE IS PLACED BELOW.
9 | OTHER BARS ARE ANY REINFORCING BARS THAT DO NOT MEET QUALIFICATION FOR TOP BARS.

## ALL_Conc_CompSplice
CONCRETE REINFORCING COMPRESSION CONTACT
SPLICE LENGTH TABLE
SPECIFIED YIELD STRENGTH
(Fy) ≤ 60KSI |  | (Fy) > 60KSI
30*Db |  | (0.9*FY - 24)Db
NOTES:
1 | SPLICE LENGTH MUST NOT BE LESS THAN 12 INCHES.
2 | Db IS BAR DIAMETER.
3 | COMPRESSION SPLICES PERMITTE ONLY WHEN LAP SPLICE IS NOTED
IN DRAWINGS AS COMPRESSION, OTHERWISE SEE TENSION SPLICE
TENSION SPLICE TABLE.

## ALL_CMU_Strength
MASONRY STRENGTH TABLE |  |  | ENGINEER NOTES:
ELEMENT |  | SPECIFIED STRENGTH | 1. CLAY MASONRY IS NOT PREFERRED.
CLAY MASONRY |  | f'm = 2500 PSI | 2. DO NOT INCLUDE BOTH CLAY AND CONC MASONRY
GROUT FOR CLAY MASONRY |  | f'g ≥ f'm (2000 PSI MINIMUM)
CONCRETE MASONRY |  | f'm = 2000 PSI
GROUT FOR CONCRETE MASONRY |  | f'g ≥ f'm (2000 PSI MINIMUM)
MASONRY REINFORCEMENT |  | Fy = 60 KSI
NOTES:
1. | PROVIDE MEDIUM WEIGHT HOLLOW CONCRETE MASONRY UNITS
FOR GENERAL USE UNLESS OTHERWISE NOTED.
2. | MORTAR FOR CONCRETE MASONRY MUST BE TYPE S AT
EXTERIOR WALLS AND TYPE N AT INTERIOR WALLS.
3. | MORTAR FOR CLAY MASONRY MUST BE TYPE S.

## PEMB Reaction Schedule
ENGINEER NOTES:
ESTIMATED PEMB REACTIONS SCHEDULE
LOCATION |  | VERTICAL LOADS (KIPS) | [5 empty] | HORIZONTAL LOADS (KIPS)
|  | DEAD | ROOF | SNOW | CRANE | WIND | SEISMIC | DEAD | ROOF | SNOW | CRANE | WIND | WIND | SEISMIC | SEISMIC
|  |  | LIVE | [5 empty] | LIVE |  |  | (X) | (Y) | (X) | (Y)
RIGID FRAMES | A.1-1.1 | +XX | +XX | +XX | +XX | +XX / -XX | +XX / -XX | +XX | +XX | +XX | +XX | +XX / -XX | -- | ± XX | --
| A.1-2.1 | +XX | +XX | +XX | +XX | +XX / -XX | +XX / -XX | +XX | +XX | +XX | +XX | +XX / -XX | -- | ± XX | --
PORTAL FRAMES
WIND COLUMNS
NOTES:
1 | LOADS LISTED ABOVE ARE NOMINAL AND MUST BE FACTORED AS REQUIRED FOR DESIGN.
2 | ROOFTOP EQUIPMENT IS INCLUDED IN ROOF LIVE LOADS LISTED ABOVE.
3 | HORIZONTAL LOADS ARE APPLIED AT TOP OF PIER ELEVATION.
4 | REFER TO PEMB REACTION DIAGRAM ON THIS SHEET FOR SIGN CONVENTION