Editors Notes:

- Masterworks may be used to edit general notes.  Values in red will be selected by Masterworks.

- Notes in blue text include information already provided within project specifications.  Blue notes must be deleted on projects that include a specification book to avoid duplicate information.

- “CONTRACTING OFFICER” is to be selected in general notes throughout on all DoD projects.  “ENGINEER” is to be selected on projects that are for commercial construction.

- Notes labeled “EDITOR’S NOTE” should be reviewed and deleted as noted are completed.

- Width of note columns in REVIT are set to 6.25” to fill 22x34 drawing sheet.

- Please “save as” to your project folder before editing.

DESIGN CRITERIA

- Building Code:

  - INTERNATIONAL BUILDING CODE (IBC) 2021 AS AMENDED BY

    - UFC 1-200-01 w/ change 3, dated 26 FEB 2024

    - UFC 3-301-01 w/ change 1, Dated 11 apr 2023

  - edition of all referenced standards noted herein are as noted in the building code.

- vertical Loads

  - Dead Loads (includes self-weight)

    - Roof							30 PSF

      - Minimum (for uplift)				12 PSF

  - Live Loads

    - Roof (reducible per asce 7)				20 psf Minimum

    - floors (reducible per asce 7)

      - typical GROUND floor				100 psf

      - HANGARS						200 psf

      - Storage						125 psf

      - Mechanical						150 psf

  - Snow Loads

    - Ground Snow Load (Pg)				5 psf

    - Additional snow drift and sliding snow as per applicable building code, refer to s-005.

  - Construction Loads

    - Not to exceed the design live loads.

- Lateral Loads

  - Risk Category						III

  - Wind Design Criteria

    - basic design Wind Speed (V)				105 MPH

    - allowable design Wind Speed (Vasd) 			82 MPH

    - Exposure Category					C

    - Internal Pressure Coefficient

      - Partially Enclosed (FULL WIND SPEED)		+/- 0.55

    - Components and Cladding				RE: S-005

    - wind ultimate base shear

      - plan east/west (area a,d)				101 k

      - plan east/west (area b,c)				125 k

      - plan north/south (area a,d)			174 k

      - plan north/south (area b,c)			187 k

  - Seismic Design Criteria

    - Seismic Importance Factor (Ie)			1.25

    - Site Class						D

    - MAPPED SPECTRAL RESPONSE ACCELERATION

      - Short Period (SS)					0.724

      - One Second (S1)					0.226

    - DESIGN SPECTRAL RESPONSE ACCELERATION PARAMETERS

      - Short Period (SDS)					0.589

      - One Second (SD1) 					0.324

    - Seismic Design Category				D

    - Seismic Response Coefficient (CS)

      - HANGAR BAYS			 			0.123

      - ADMIN AND SHOP					0.123

    - Seismic Design Base Shear

      - Plan East/west (area a,d)				84 k

      - Plan East/west (area b,c)				79 k

      - plan north/south (area a,d)			84 k

      - plan north/south (area b,c)			79 k

    - Seismic Resisting System:

      - Steel Special Concentric Braced Frames (HANGAR)

        - RESPONSE MODIFICATION 			R = 6

        - DEFLECTION AMPLIFICATION 			Cd = 5

        - OVERSTRENGTH FACTOR 			Ωo = 2

      - SPECIAL REINFORCED MASONRY SHEAR WALLS (ADMIN AND SHOP)

        - RESPONSE MODIFICATION 			R = 5

        - DEFLECTION AMPLIFICATION 			Cd = 3.5

        - OVERSTRENGTH FACTOR 			Ωo = 2.5

    - Analysis Method: Equivalent Lateral Force Procedure

- Foundation Design Criteria

  - foundation design is based upon the following soil parameters as provided in the geotechnical engineering report listed below:

    - report agency					UES (PENDING UPDATE)

    - report #						4030.2400199

    - report date					2025-04-17

  - net allowable soil bearing pressure

    - spread footings				3000 psf

    - Continuous footings 				3000 psf

  - Lateral earth pressure parameters

    - Soil Density					120 PCF

    - Angle of Internal Friction			30 degrees

    - Coefficient of Friction (u)			0.36

    - Wind/Seismic increase				1/3 INCREASE

    - Passive Earth Pressure (Kp)			3.00

  - Modulus of Sub-grade Reaction (ks)		120 pci

  - minIMUM bearing depth				24 inches

DC-5 	ANTITERRORISM (AT) CRITERIA

- THIS FACILITY HAS BEEN DESIGNED IN ACCORDANCE WITH THE ANTITERRORISM REQUIREMENTS SET FORTH IN UFC 4-010-01, DATED 24 MAY 2024.  BUILDING ANTITERRORISM STRUCTURAL DESIGN CRITERIA ARE AS FOLLOWS:

- AT FACILITY CRITERIA

  - STANDARD 1:	BUILDING STANDOFF DISTANCE	> 50 FT TO PERIMETER

  - STANDARD 2:	UNOBSTRUCTED SPACE	33 FT

  - STANDARD 5:	PARKING BENEATH BUILDINGS

OR ON ROOFTOPS	N/A

  - STANDARD 6:	PROGRESSIVE COLLAPSE	N/A

  - STANDARD 7:	STRUCTURAL ISOLATION	N/A

  - STANDARD 8:	BUILDING OVERHANGS AND

BREEZEWAYS	N/A

  - STANDARD 9:	EXTERIOR MASONRY WALLS	#5@32” OC MAX

VERTICAL REINF

  - STANDARD 15:	OVERHEAD MOUNTED ARCH

FEATURES	RE: DELEGATED
DESIGN

  - STANDARD 19:	EQUIPMENT BRACING	RE: DELEGATED
		DESIGN

GENERAL

- Methods, procedures and sequences of construction are the responsibility of the Contractor.  The Contractor is responsible for implementing the necessary precautions to maintain the integrity of the structure at EACH stage of construction.

- structural engineer will not be responsible for activities under the control of the contractor such as construction site safety, means, methods and sequences of construction.  structural engineer will not be responsible for fabrication, erection and construction requirements as prescribed by osha or other regulatory agencies regardless of indication in these documents.  the contractor is soley responsible for all safety regulations, programs and precautions related to all work on the project.

- where supported slabs or roofs are to be used for staging or temporary construction loads, the contractor must verify that applied loads do not exceed the design loads for the supporting floorS or roofs.  during and after construction, contractor and/or contracting officer must keep loads on the structure within the limits of the design loads as noted in these drawings.

- THE STRUCTURAL SYSTEMS SHOWN IN THESE DRAWINGS MUST NOT BE CONSIDERED STABLE UNTIL ALL STRUCTURAL ELEMENTS ARE IN PLACE AND COMPLETED.  Temporary bracing, sheeting, shoring, etc, required to ensure the structural integrity/stability of the existing buildings, sidewalks, utilities, etc, during construction is the responsibility of the Contractor and must be designed by a Registered Professional Engineer employed by the contractor.

- When not specifically indicated on the structural drawings, the contractor is responsible for determining sleeve and block-out requirements for penetrations prior to fabrication or erection of the structure.  Penetrations of structural members are subject to approval by the EOR.  The Contractor is also responsible for determining anchorage and hanger requirements required for supporting equipment, finishes, utilities et cetera not indicated on the structural drawings.

- CONTRACTOR MUST COORDINATE WITH ALL TRADES THE LOCATIONS AND DIMENSIONS OF ALL OPENINGS THROUGH FLOORS, ROOFS AND WALLS REGARDLESS OF IF THEY ARE SHOWN ON THE STRUCTURAL DRAWINGS.

- The Contractor is responsible for coordinating dimensions and installation requirements of equipment with the supporting structure.

- THE STRUCTURAL DRAWINGS ARE SUPPLEMENTARY TO THE ARCHITECTURAL AND OTHER DISCIPLINE DRAWINGS. DO NOT ATTEMPT TO BID NOR CONSTRUCT ANY PORTION OF THIS PROJECT WITHOUT CONSULTING OTHER DISCIPLINES’ DRAWINGS WITHIN THIS PROJECT. ALL CONFLICTS OR OMISSIONS, INCLUDING DIMENSIONS, BETWEEN THE VARIOUS ELEMENTS OF THE STRUCTURAL DRAWINGS AND/OR SPECIFICATIONS MUST BE BROUGHT TO THE ATTENTION OF THE ARCHITECT AND ENGINEER BEFORE PROCEEDING WITH ANY WORK INVOLVED. IN CASE THERE IS A CONFLICT BETWEEN DRAWINGS, SUBMIT A REQUEST FOR INFORMATION, AND PROCEED AS DIRECTED BY THE ENGINEER. ANY WORK DONE BY THE CONTRACTOR AFTER DISCOVERY OF SUCH DISCREPANCY WITHOUT OFFICIAL DIRECTION WILL BE DONE AT THE CONTRACTOR’S RISK.

- FIREPROOFING, IF REQUIRED, OF STRUCTURAL ELEMENTS IS NOT SHOWN ON THE STRUCTURAL DRAWINGS. REFER TO THE SPECIFICATIONS, FIRE PROTECTION DRAWINGS AND/OR ARCHITECTURAL DRAWINGS.

- In case of conflict between the General Notes, Specifications, Drawings, OR WITHIN THESE DOCUMENTS, the most stringent requirements as determined by the ENGINEER will govern.

- Work not indicated on a part of the drawings, but reasonably implied to be similar to that shown at corresponding locations, is to be repeated.

- TYPICAL DETAILS ARE GENERALLY NOT REFERENCED ON THE DRAWINGS AND WILL APPLY IN AREAS WHERE CONDITIONS ARE SIMILAR AS DESCRIBED IN THE DETAILS.  THE CONTRACTOR MUST IDENTIFY, COORDINATE AND APPLY THESE DETAILS AS NEEDED.  TYPICAL DETAILS MAY BE REFERENCED ON PLANS OR DETAILS TO CLARIFY OR IDENTIFY A PARTICULAR CONDITION. THE PRESENCE OF SUCH A REFERENCE DOES NOT ALTER THE OBLIGATION OF THE CONTRACTOR TO APPLY THE DETAIL(S) AS NEEDED EVEN IF THEY ARE NOT REFERENCED.

- THE STRUCTURAL DOCUMENTS HAVE BEEN DRAWN TO SCALE AS INDICATED ON THESE DRAWINGS.  THIS IS TO CONFIRM GENERAL GEOMETRIC TOLERANCES TO THE GREATEST EXTENT POSSIBLE. HOWEVER, SOME COMPONENTS MAY NOT BE DRAWN TO SCALE TO REFLECT DESIGN INTENT.  IF DIMENSIONAL INFORMATION IS NOT INDICATED AND/OR PROVIDED, THE ENGINEER MUST BE NOTIFIED IN WRITING.  DO NOT SCALE DRAWINGS.

CONSTRUCTION ADMINISTRATION

- CONTRACTOR IS RESPONSIBLE FOR VERIFYING ALL SIZES, DIMENSIONS, AND ELEVATIONS ON SUBMITTALS AS RELATED TO DESIGN DOCUMENTS PRIOR TO DELIVERY TO THE ENGINEER FOR REVIEW.

- PREPARATION OF SHOP DRAWING SUBMITTALS FOR STRUCTURAL ELEMENTS WILL REQUIRE INFORMATION (I.E. DIMENSIONS, ETC.) FOUND IN THE ARCHITECTURAL, MECHANICAL, ELECTRICAL, PLUMBING AND OTHER DISCIPLINE DRAWINGS.  CONTRACTOR IS TO FURNISH SUFFICIENT INFORMATION, INCLUDING PROJECT SPECIFICATIONS, to the SUB-CONSULTANT CREATING THE SHOP DRAWING SUBMITTAL TO ALLOW FOR A COMPETE SUBMITTAL.

- Shop drawings:

  - Shop drawings for materials must be submitted to the ENGINEER AND CONTRACTING OFFICER for review prior to the start of fabrication or commencement of work.

  - Shop drawings must be checked and stamped by the Contractor prior to submission.  The Contractor’s stamp of approval will constitute certification that he has verified field measurements, construction criteria, materials and similar data and has checked each drawing for completeness, coordination, and compliance with the Contract Documents. SHOP DRAWINGS SUBMITTED WITHOUT THE CONTRACTOR’S STAMP AND REVIEW WILL BE RETURNED WITHOUT REVIEW BY THE ENGINEER.

  - Reproduction of any portion of the Structural Contract Drawings for submittal as shop drawings is prohibited.  SUBMITTALS PROVIDED THAT INCLUDE REPRODUCTION OF THE CONTRACT DRAWINGS WILL BE RETURNED WITHOUT REVIEW BY THE ENGINEER.

  - Changes to shop drawings that are re-submitted must be clouded or somehow indicate that a change has been made to previously issued and reviewed drawingS.  REVISED SHOP DRAWINGS PROVIDED WITHOUT CLOUDS OR CHANGES INDICATED WILL BE RETURNED WTIHOUT REVIEW BY THE ENGINEER.

  - The contractor is to provide the ENGINEER AND Contracting Officer with written notice of deviations of any type from the requirements of the Construction Documents.  The notice must be received prior to shop drawing submittal.  The Contractor remains liable for any deviation unless reviewed by the ENGINEER AND Contracting Officer and acknowledged in writing, prior to the receipt of the shop drawings.

  - CONTRACTOR IS NOT RELIEVED OF ANY REQUIREMENT OF THE CONTRACT DOCUMENTS BY VIRTUE OF ENGINEER OR CONTRACTING OFFICER REVIEW OF SUBMITTALS.

  - REVIEW OF SUBMITTALS BY THE ENGINEER IS FOR GENERAL COMPLIANCE WITH THE CONTRACT DOCUMENTS ONLY AND IS NOT INTENDED AS APPROVAL.

- unless noted otherwise, allow 10 business days for THE ENGINEER’s review.

- A QUALIFIED TESTING AGENCY MUST PERFORM TESTS AND SPECIAL INSPECTIONS. UPON COMPLETION OF WORK, THE TESTING AGENCY MUST FURNISH A CERTIFICATE OF COMPLIANCE, SIGNED BY THE PROFESSIONAL ENGINEER RESPONSIBLE FOR MANGEMENT OF THE AGENCY.  tHE PROFESSIONAL ENGINEER MUST BE REGISTERED IN THE UNITED STATES.

FOUNDATIONS

- foundations have been designed and must be constructed in accordance with the geotechnical report for this project as listed in the design criteria WHICH is considered aS THE BASIS OF FOUNDATION DESIGN. CONTRACTOR IS RESPONSIBLE FOR REVIEWING AND UNDERSTANDING REQUIREMENTS SET FORTH WITHIN THE REPORT AS THEY APPLY TO THIS FOUNDATION DESIGN.  THE STRUCTURAL ENGINEER IS NOT LIABLE OR RESPONSIBLE FOR THE ACCURACY OF RECOMMENDATIONS PRESENTED WITHIN THE GEOTECHNICAL REPORT.

- Foundations MUST be placed on A MINIMUM OF 30” LAYER OF compacted SELECT fill AND A 6” LAYER OF SCARIFIED RE-COMPACTED SUBGRADE, conforming to recommendations provided in the Geotechnical report (maximum fill lift = 8”).

- The contractor is to retain the services of a professional Geotechnical Engineer, subject to the approval of the Contracting Officer, to verify that the material on which foundations bear has at least the capacity as noted in the Design Criteria. PRIOR TO PLACING CONCRETE, AND AFTER COMPACTION OF SUBGRADE, ALL FOUNDATION EXCAVATIONS SHALL BE INSPECTED AND TESTED which must INCLUDE IN PLACE DENSITY TESTING. if the subgrade has less than the stated allowable bearing capacity, the weak subgrade shall be removed, recompacted, and retested until it is satisfactory at no additional cost to the owner. concrete placement shall not proceed until the subgrade meets the minimum density requirements of the specifications and the geotechnical report, whichever is more stringent.

- EXTERIOR FOUNDATONS ARE TO BEAR BELOW THE MINIMUM BEARING DEPTH FROM FINISHED GRADE GIVEN IN DESIGN CRITERIA GENERAL NOTE DC-4.  INTERIOR FOUNDATIONS TO BEAR THE MINIMUM BEARING DEPTH OR AS INDICATED.  FINAL BEARING ELEVATIONS MAY VARY TO SUIT SUBSURFACE SOIL CONDITIONS OR BELOW GRADE UTILITIES.   NOTIFY THE ENGINEER AND CONTRACTING OFFICER OF ANY CHANGES. PROVIDE FOUNDATION STEPS AS NECESSARY.

- No backfilling against walls is ALLOWED until the slabs at the top and bottom have been placed or adequate shoring has been provided.  Walls and grade beams having backfill against both sides are to have backfill placed on both sides uniformly so as not to exceed an 8” differential.

- foundation drainage, insulation and/or waterproofing is not shown or specified within the structural portion of the construction documents.  reference other portions of the construction documents for drainage, insulation and/or waterproofing, or items associated with other disciplines.

REINFORCED CONCRETE

- Reinforced concrete work MUST be in accordance with the American Concrete Institute (ACI) "Building Code Requirements for Structural Concrete - ACI 318" and the “Specifications for Structural Concrete for Buildings- ACI 301.”

- MAXIMUM MIX DESIGN W/C RATIO MUST NOT BE EXCEEDED. APPROVED ADMIXTURES SUCH AS PLASTICIZERS OR SUPERPLASTICIZERS MAY BE USED ON SITE TO INCREASE SLUMP AND FLOWABILITY AS REQUIRED FOR PLACEMENT. REFER TO ACI 311.5 FOR DOCUMENTATION REQUIREMENTS AND IBC CHAPTER 1703 FOR INSPECTION REQUIREMENTS.

- Cast-in-place concrete must have a minimum 28 day compressive strength (f'c) as indicated on the Concrete mix design table.

- THE STRUCTURE SUPPORTING ELEVATED FLOORS IS DESIGNED TO HAVE AN INITIAL (PRE-COMPOSITE) DEFLECTION OF NOT MORE THAN ¾” DUE TO THE WEIGHT OF THE CONCRETE SLAB.  THE CONTRACTOR MUST TAKE THIS DEFLECTION INTO ACCOUNT WHEN DETERMINING THE AMOUNT OF CONCRETE NECESSARY TO OBTAIN A LEVEL FLOOR AND MONITOR DEFLECTION DURING CONCRETE PLACEMENT.

- REINFORCEMENT AND EMBEDDED ITEMS:

  - PROVIDE STANDARD HOOKS ON BARS TERMINATING AT A CONCRETE FACE UNLESS NOTED SUCH AS AT EDGES OF OPENINGS, SLAB EDGES, EXPANSION JOINTS, ENDS OF BEAMS AND ENDS OF WALLS.

  - see concrete reinforcement development length and splice table for all required development and splice lengths.

  - PROVIDE ADEQUATE CONCRETE COVER IN ACCORDANCE WITH THE REQUIREMENTS AS SET FORTH BY ACI 318 AND AS PROVIDED WITHIN THE CONCRETE COVER TABLE IN THE SPECIFICATIONS.

  - HOOKED BARS TO HAVE STANDARD ACI HOOKS UNLESS NOTED OTHERWISE.  UNLESS NOTED OTHERWISE, HOOKS CAN BE ORIENTED AS REQUIRED.

  - CONTINUOUS REINFORCING BARS MUST BE TURNED AND LAPPED AT CORNERS AND INTERSECTIONS OF WALLS AND FOOTINGS.

  - welding of reinforcement is prohibited, unless noted otherwise and must conform to astm a 706.

  - provide embeds (including anchors), as required, for all supporting non-structural elements including but not limited to hand rails, canopies, window washiNG davits, miscellaneous steel, etc.  refer to architectural and mep drawings for additional information.

- Concrete slabs MUST BE cured by method compatible with specified floor finish.  Where acceptable use A LIQUID MEMBRANE-CURING COMPOUND AT THE MANUFACTURERS RECOMMENDED COVERAGE.

- CONCRETE SLAB CONTROL JOINT PLACEMENT AND LAYOUT PER GC AND SUBMITTED AS SHOP DRAWING FOR REVIEW.

- Sleeves, inserts, mechanical openings, conduits, pipes, recesses, Depressions, curbs and other embedded items must be PROVIDED AS shown on the architectural, mechanical, fire protection, plumbing and electrical drawings and by equipment manufacturers.  Installation of these items must be coordinated and provided for prior to placing concrete.

- OPENINGS IN CONCRETE SLABS AND/OR CONCRETE WALLS MUST HAVE ADDITIONAL REINFORCEMENT PER THE TYPICAL DETAILS.  NO PENETRATIONS ARE PERMITTED THROUGH ANY CONCRETE BEAM, JOIST, COLUMN, PIER OR JAMB WITHOUT THE ENGINEER’S WRITTEN APPROVAL.  PENETRATIONS MUST BE RE-ROUTED AS REQUIRED AT THESE LOCATIONS.

- PENETRATIONS THROUGH CONCRETE SLABS AND/OR CONCRETE WALLS MUST BE PLACED DURING CONSTRUCTION OF THE WALL WITH THE APPROPRIATE SLEEVE.

- REFER TO CONCRETE TABLES ON S-004 FOR ADDITIONAL INFORMATION.

MASONRY

- Masonry work must be in conformance with the Masonry Society (TMS) “building code requirements for masonry structures – tms 402” and the “Specifications for Masonry Structures – tms 602”.

- REINFORCEMENT AND EMBEDDED ITEMS:

  - REINFORCING TO BE DISCONTINUOUS AT CONTROL JOINTS UNESS NOTED OTHERWISE.  BOND BEAM REINFORCING AT THE TOPs AND BOTTOMs OF WALLS IS TO BE CONTINOUS THROUGH JOINT.

  - DOWEL REINFORCED MASONRY WALLS TO FOUNDATION.  SIZE DOWELS TO MATCH WALL REINFORCEMENT.  LOCATE DOWELS IN CELLS TO CONTAIn WALL REINFORCEMENT.  LAP DOWELS WITH WALL REINFORCEMENT PER MASONRY LAP TABLE.

  - Unless noted otherwise, place typical CMU reinforcement in center of fully grouted cells and space as follows:

    - For 8” CMU: (1) #5 vertical at 32” on center, minimum.

    - For 12” CMU: (1) #5 vertical at 24” on center, miminum.

    - Provide additional bars at corners and openings per typical details.

  - VERTICAL REINFORCING TO BE HELD SECURELY IN PLACE DURING GROUt PLACEMENT TO PREVENT DISPLACEMENT OF REINFORCEMENT.

  - WELDING OF REINFORCEMENT IS PROHIBITED, UNLESS NOTED OTHERWISE.

  - PROVIDE EMBEDS (INCLUDING ANCHORS) FOR SUPPORTING STRUCTURAL AND NON-STRUCTURAL ELEMENTS INCLUDING BUT NOT LIMITED TO: HANDRAILS, CANOPIES, MISCELLANEOUS STEEL, ETC.

- MASONRY ERECTION:

  - GROUT CELLS SOLID AT: INSERTS, ANCHORS, AND ELEVATOR GUIDE RAILS IN ADDITION TO LOCATIONS SHOWN IN THE TYPICAL DETAILS.

  - DO NOT FULLY GROUT WALLS UNLESS SPECIFICALLY CALLED OUT ON STRUCTURAL DRAWINGS.

  - control joint spacing in masonry walls must be provided where indicated on the Structural Drawings, or a maximum of 24'-0" on center.

  - masonry walls to be temporarily braced until floor or roof system has been installed and has become capable of stabilizing the walls.

  - COORDINATE BLOCKOUTS, REVEALS, HOLES, OPENINGS AND BUILT-IN ITEMS WITH ALL CONTRACT DOCUMENTS AND DISCIPLINES.

  - Provide vertical MASONRY VENEER control joints as indicated on the Architectural Drawings.

- REFER TO MASONRY TABLES ON S-004 FOR ADDITIONAL INFORMATION.

POST-INSTALLED ANCHORS

- ALL ADHESIVE OR MECHANICAL ANCHORS MUST BE INSTALLED, INCLUDING HOLE DRILLING, DRILL BIT TYPE, PREPARATION, AND CLEANING IN ACCORDANCE WITH AN APPROVED INDEPENDENT EVALUATION REPORT (ICC-ES, IAPMO, OR APPROVED EQUAL), THE project DRAWINGS AND SPECIFICATIONS, AND IN ACCORDANCE WITH ALL MANUFACTURER’S PRINTED INSTALLATION INSTRUCTIONS (MPII).

- POST-INSTALLED ANCHORS HAVE BEEN DESIGNED WITH HILTI ANCHORS (NOTED BELOW) AS THE BASIS OF DESIGN.  PROVIDE APPROPRIATE ANCHOR WITH SIZE AND FINISH AS NOTED AND EQUIVALENT SHEAR AND TENSION CAPACITIES AFTER MODIFICATION DUE TO EMBEDMENT, SPACING AND EDGE DISTANCES.  OTHER AVAILABLE MANUFACTURERS INCLUDE SIMPSON, ITW RED HEAD AND DEWALT.

  - EXPANSION ANCHORS:	KWIK BOLT 3

  - SCREW ANCHORS:		KH-EZ SCREW ANCHOR

  - ADHESIVE ANCHORS

    - CONCRETE:		HIT HY-200

    - GROUTED CMU:		HIT HY-270

  - SCREEN TUBE ANCHORS:	HIT HY-270

- SUBSTITUTION REQUEST FOR ALTERNATIVE PRODUCTS MUST BE APPROVED IN WRITING BY THE STRUCTURAL ENGINEER PRIOR TO THE USE. SUBSTITUTION REQUEST MUST INCLUDE AN APPROVED INDEPENDENT EVALUATION REPORT (ICC-ES, IAPMO OR APPROVED EQUAL) AND SUPPORTING CALCULATIONS INDICATING COMPLIANCE WITH DESIGN INTENT. SUBSTITUTIONS MUST BE EVALUATED FOR THEIR COMPLIANCE with relevant building codes for seismic uses, load resistance, INSTALLATION CATEGORY, AND AVAILABILITY OF COMPREHENSIVE INSTALLATION INSTRUCTIONS. ADHESIVE ANCHOR EVALUATIONS must CONSIDER HINSTALLED SUBSTITUTION ANCHORS IN CONCRETE MUST BE SUITABLE FOR USE IN CRACKED CONCRETE APPLICATIONS.

- DO NOT DISTURB, MAKE ATTACHMENTS, OR APPLY LOAD TO ADHESIVE ANCHORS PRIOR TO THE FULL CURE OF THE ADHESIVE.  ADHESIVE ANCHORS MUST NOT BE FULLY LOADED UNTIL CONCRETE HAS REACHED 28-DAY DESIGN STRENGTH.

- CONCRETE TEMPERATURE AT THE TIME OF INSTALLATION MUST BE MONITORED BY THE CONTRACTOR.  CONTRACTOR MUST COMPLY WITH ALL MANUFACTURER’S PRINTED INSTALLATION INSTRUCTIONS RELATIVE TO SUBSTRATE TEMPERATURE.

- INSTALLATION OF ADHESIVE ANCHORS HORIZONTALLY OR UPWARDLY INCLINED TO SUPPORT SUSTAINED TENSION LOADS MUST BE PERFORMED BY PERSONNEL CERTIFIED BY AN APPLICABLE CERTIFICATION PROGRAM.  CERTIFICATION MUST INCLUDE WRITTEN AND PERFORMANCE TEST IN ACCORDANCE WITH THE ACI/CRSI ADHESIVE ANCHOR INSTALLER CERTIFICATION PROGRAM, OR APPROVED EQUIVALENT, IN ACCORDANCE WITH ACI.  PROOF OF CURRENT CERTIFICATION MUST BE SUBMITTED TO THE ENGINEER AND CONTRACTING OFFICER FOR APPROVAL PRIOR TO INSTALLATION.  CONTINUOUS SPECIAL INSPECTION IS REQUIRED FOR THESE ANCHORS.

- IF REINFORCING IS ENCOUNTERED DURING DRILLING, THAT HOLE IS TO BE ABANDONED.  DO NOT DAMAGE REINFORCING TO MAINTAIN STRUCTURAL INTEGRITY OF SUBSTRATE COMPONENT. FILL ABANDONED HOLES WITH NON-SHRINK GROUT AND COnTACT THE STRUCTURAL ENGINEER FOR NEW LOCATIONS AND FURTHER INSTALLATION INSTRUCTIONS.

- POST-INSTALLED ANCHORS TO BE GALVANIZED WHERE EXPOSED TO EXTERIOR AND/OR CORROSIVE ENVIRONMENTS UNLESS THE ANCHOR IS OTHERWISE PROTECTED.

- SUBSTITUTION OF POST-INSTALLED ANCHORS FOR EMBEDDED ANCHORS SHOWN ON THE DRAWINGS IS NOT PERMITTED.

STRUCTURAL STEEL

- Structural steel work is to be detailed and constructed in accordance with THE FOLLOWING STANDARD(S):

  - the American Institute of Steel Construction (AISC) 360 "Specifications for Structural Steel Buildings"

  - The american institute of steel construction (AISC) 341 “Seismic provisions for structural steel buildings”

- Prior to fabrication, the steel fabricator is to submit to the Contracting Officer for review Shop drawings showing erection plans, piece drawings, and connection details.

- Structural Steel Fabricator is to provide for vertical and horizontal field adjustment of support assemblies.

- Steel beams are to be equally spaced in bays unless otherwise noted.

- Fabricate and install beams with natural camber up unless camber is noted on the drawings.

- structural steel frames and trusses are to be securely braced until floor slabs, roof decks and shear walls have been installed and become capable of stabilizing the frames.

- Unless otherwise noted, structural steel connections to be shop welded and field bolted.

- BOLTED CONNECTIONS:

  - Bolts, TYPICAL: 3/4" MINIMUM diameter ASTM F 3125 GR. a325N UNO with matching washers and heavy hex nuts. BOLTS MUST BE INSTALLED IN A SNUG TIGHT CONDITION WHICH IS ACHIEVED WHEN CONNECTED PARTS ARE IN FIRM CONTACT.

  - DO NOT REUSE ANY BOLTS, NUTS, AND/OR WASHERS.

  - DO NOT APPLY ANY WELD TO BOLTS, NUTS, OR WASHERS UNO.

- WELDED CONNECTIONS:

  - USE E70XX ELECTRODES UNLESS OTHERWISE INDICATED ON THE DRAWINGS.  E60XX MAY BE USED FOR WELDING cold-formed steel decks and framing.

  - WELDING OF DEFORMED BAR ANCHORS AND/OR HEADED STUD ANCHORS IS TO BE IN ACCORDANCE WITH MANUFACTURER’S SPECIFICATIONS.

  - FILLET WELD SIZES NOT DESIGNATED MUST BE THE SAME AS THE THINNEST CONNECTED PARTS OR ¼-inch FILLET WELD ALL AROUND.

- Substitution of post-installed anchors for embedded anchors shown on the drawings is not permitted.

- Paint and protection:

  - Exposed structural steel to receive painted finish to be shop cleaned and prime painted in accordance with specification section 05 12 00 part 2 - products.  Reference architecture for finish paint systems.

  - Exposed structural steel for screen walls, equipment platforms, loose angle lintels etc, to be hot dipped galvanized per ASTM A 123

  - Galvanized fasteners and accessories to be hot dipped galvanized per ASTM A 153/A 153M.

  - Provide minimum 3” concrete cover for steel below grade.

MISCELLANEOUS STEEL

- COORDINATE ALL MISCELLANEOUS steel ITEMS WITH STRUCTURAL STEEL NOTES.

- Prior to fabrication, the steel fabricator is to submit THE FOLLOWING to the Contracting Officer for review:

  - Shop drawings showing erection plans, piece drawings, and connection details.

- Manufacture steel grating in accordance with the “Metal Bar Grating Manual” as published by the National Association of Architectural Metal Manufacturers.

  - Steel for grating to conform to ASTM A 1011/A 1011M.  Grating to be type W-19-6 (1”x3/16”) with galvanized finish.

  - Aluminum for grating to conform to ASTM B 221.  Grating to be type as noted with mill finish, UNO.

OPEN WEB STEEL JOISTS

- Design, fabrication and erection of open web steel joists must conform to the Steel Joist Institute (SJI) "Standard Specifications and Load Tables for Steel Joists and Joist Girders."

- Design ALL JOISTS, INCLUDING SLOPE, CAMBER AND BEARING ENDS.  provide ALL BRIDGING LOCATIONS AND LAYOUTS. ALL DESIGNS MUST BE IN ACCORDANCE WITH SJI SPECIFICATIONS WITH A MAXIMUM DEFLECTION OF TL/180 AND LL/240.

- Steel joists are to be designed for all loads indicated as well as wind uplift as shown on Sheet S-005.

- Provide bridging, BOTTOM CHORD EXTENSIONS and ASSOCIATED anchorage in accordance with SJI requirements.  BRIDGING, BOTTOM CHORD EXTENSIONS AND ASSOCIATED ANCHORAGE IS BY THE JOIST MANUFACTURER UNLESS NOTED OTHERWISE. Where erection bridging is required, have in place a row of bolted bridging before releasing hoist lines.

- Bottom chord extensions to be installed AS REQUIRED BY OSHA AND THE STEEL JOIST SUPPLIER. DO NOT FULLY CONNECT EXTENSIONS TO THE SUPPORTING STRUCTURE UNTIL APPLICABLE DEAD LOAD HAS BEEN APPLIED.

- Steel joist manufacturer is to provide additional bottom chord BRIDGING FOR uplift loads.

- provide anchors and fasteners required for installation of joists, bridging and bottom chord extensions.

- Steel joists are to be equally spaced in bays uno.  Do not exceed joist spacing indicated on the drawings.

- Joist seats have been assumed to be as listed below, UNO.  modifications to the structure for alternate depths must be coordinated by the General Contractor.

  - ALL SERIES:  	5”

- Hangers supporting mechanical, electrical or other equipment are to be placed at joist panel points (welding not permitted) and applied loads are to be coordinated with steel joist manufacturer.  Do not suspend equipment from bridging or metal deck.

- Steel joist manufacturer to verify size, location and weight of supported mechanical units and associated openings prior to fabrication.

METAL DECK

- Metal deck must be detailed in accordance with the Steel Deck Institute (SDI) "Design Manual for Composite Decks, Form Decks and Roof Decks".

- Deck units HAVE BEEN DESIGNED to be a minimum of three (3) spans continuous with laps placed over supports.

- REFER TO ROOF DECK SCHEDULE ON S-603 WHICH INCLUDES DEPTH PROFILE, THICKNESS, AND ATTACHMENT.

LIGHT GAGE STEEL FRAMING

- Structural members must be designed in accordance with the American Iron and Steel Institute (AISI) "North American Specification for the Design of Cold-Formed Steel Structural Members" (latest edition).

- Structural members to be formed from corrosion resistant steel conforming to ASTM A 653/A 653M with minimum yield stress (Fy) according to structural performance.

- Light gage members and details shown on the Architectural or Structural drawings are for bid purposes only.  Structural stud and/or joist framing members and connections are to be engineered by the manufacturer.  Design calculations and shop drawings indicating jambs, posts, headers, bracing and pieces necessary for construction must be submitted to the Contracting Officer FOR review.  Design calculations are to be prepared by or under the supervision of a Professional Engineer registered in the United States and bearing the seal of that Professional Engineer.

- Maximum stud spacing to be 16” on center with doubled studs (minimum) at each side of openings.

- Framing components are to be cut squarely for attachment to perpendicular members or as an angular fit against abutting members.

- Field cutting of studs must be done by sawing or shearing, torch cutting of cold-formed members is unacceptable.

- Fastening of components is to be with self-drilling screws or welding. Welding of studs must comply with AWS D1.3/D1.3M. welds to be touched-up with zinc-rich paint. Screws and welds to be of sufficient size to ensure the strength of the connection.  Wire tying of components is not permitted.

- Light gage steel framing members are to be securely attached to the structure where indicated on the drawings or approved shop drawings.  Fasteners to be compatible with the structural members.  Powder driven fasteners are not acceptable for structural applications.

- Provide vertical slide tracks, or slide clips, where indicated on the drawings or otherwise required to allow for vertical structural movements.  Maximum expected structure live load deflection is L/360 at floors and L/240 at roofs.

- Reference Architectural drawings for additional information, including sheathing type, finishes, openings, locations etc.